Twin City Fan & Blower Guide Specification
Propeller Fans: Model TCWPF, Direct Drive

Twin City Fan & Blower Model TCWPF Series, Fiberglass Direct Drive Propeller Type Fan is designed to withstand corrosive environments. The TCWPF's standard housing is fabricated with an integral inlet side mounting flange. It incorporates a solid FRP motor base that is reinforced with solid FRP support struts.

Application

Constructed of fiberglass reinforced plastic (FRP), the TCWPF is primarily used for general space exhaust of gases, fumes and vapors from chemical processes. The TCWPF’s propeller is constructed of glass cloth impregnated with vinyl ester resin and secured to the motor shaft.

Sizes (Propeller Diameter): 12 to 48 inches (305 to 1,219 mm)

Airflow: 	Up to 41,900 CFM (71,187 m3/hour)

Static Pressure: Up to 1 inch wg (248 Pa)

Airstream Temperature: 200 deg. F (93 deg. C), maximum.

Twin City Fan & Blower (TCF) is an industry leading designer and manufacturer of high quality commercial and industrial fans and is a division of Twin City Fan Companies, Ltd. Our extensive product line includes centrifugal fans and blowers, axial fans, and power roof ventilators. For the commercial market, TCF supplies ventilation fans for retail and office buildings, restaurants, schools, hospitals, and government buildings. TCF’s industrial fans are used in a wide variety of process applications for numerous industries including Petrochemical, Nuclear, Cement, Steel, and Air Pollution Control. Special materials, construction, coatings, and accessories are available to fit any application requirements.

TCF has completed thousands of successful installations across the globe and has a proven track record for tackling the most technically complex applications within the fan industry. TCF is also known for its technical design capabilities, comprehensive testing services, and responsive sales team. Due to the company’s extensive expertise and long-standing reputation for proven quality, TCF products continue to be specified around the globe.

TCF occupies over 1,000,000 sq. ft. of manufacturing space across ten facilities in the U.S, with expanded manufacturing and service operations located in South America, Europe, India, China, and Singapore. Headquarters are located in Minneapolis, Minnesota, which houses the management, sales and marketing, accounting, human resources, material management, engineering personnel, as well as a state-of-the-art AMCA accredited testing lab.

We recommend you consult with your Twin City Fan & Blower Sales Representative, who can be contacted through: Twin City Fan & Blower, Minneapolis MN; (763) 551-7600; email: tcf_sales@tcf.com; www.tcf.com.

This document Copyright© 2015 Twin City Fan & Blower

SECTION 23 34 23.04 – PROPELLER FANS

GENERAL

SUMMARY

Section includes fiberglass propeller type wall fans, with direct drive.

REFERENCE STANDARDS

Air Movement and Control Association International, Inc. (AMCA): www.amca.org:

AMCA Standard 204 - Balance Quality and Vibration Levels for Fans

AMCA Standard 210 - ASHRAE 51 - Laboratory Methods of Testing Fans for Certified Aerodynamic Performance Rating

AMCA Standard 300 - Reverberant Room Method for Sound Testing of Fans

ASTM International (ASTM): www.astm.org

ASTM E84 - Standard Test Method for Surface Burning Characteristics of Building Materials

National Electrical Manufacturers Association (NEMA): www.nema.org

NEMA MG 1 – Motors and Generators

National Fire Protection Association (NFPA): www.nfpa.org:

NFPA 70 - National Electric Code

ACTION SUBMITTALS

Product Data: Include the following:

Rated capacities and operating characteristics.

Fan Performance Data: Fan performance curves with flow, static pressure and horsepower.

Sound Performance Data: Fan sound power levels in eight octave bands and, A-weighted overall sound power level or sone values.

Motor ratings and electrical characteristics.

Furnished specialty components.

Specified accessories.

Dimensioned standard drawings indicating dimensions, weights, and attachments to other work.

Specifier: If Contractor will be required to provide engineering drawings and calculations for vibration, seismic, or high wind design, insert requirements here.

INFORMATIONAL SUBMITTALS

Source quality-control reports.

Field quality-control reports.

ISO-9001 certificate.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data: Include routine maintenance, adjustment requirements, safety information, and troubleshooting guide.

QUALITY ASSURANCE

Manufacturer Qualifications:  Approved ISO 9001-compliant manufacturer listed in this Section with minimum 10 years' experience in manufacture of similar products in successful use in similar applications, and with an ASME NQA-1 compliant Program.

Specifier:  Retain paragraph below if Owner allows substitutions but requires strict control over qualifying of substitutions.

Approval of Comparable Products:  Submit the following in accordance with project substitution requirements, within time allowed for substitution review:

Product data, including certified independent test data indicating compliance with requirements.

Project references:  Minimum of 5 installations not less than 5 years old, with Owner contact information.

Sample warranty.

Substitutions following award of contract are not allowed except as stipulated in Division 01 General Requirements.

Approved manufacturers must meet separate requirements of Submittals Article.

AMCA Compliance:

Provide fan types tested in accordance with AMCA Standard 210 (air performance) and AMCA Standard 300 (sound performance) in an AMCA-accredited laboratory.

COORDINATION

Coordinate sizes and locations of supports required for fan units.

Coordinate sizes and locations of equipment supports and building penetrations.

FIELD CONDITIONS

Handling and Storage: Handle and store fan units in accordance with manufacturer's published instructions. Examine units upon delivery for damage. Store units protected from weather.

WARRANTY

Specifier: Consult TCF for available special Project-specific warranties.

Manufacturer's Warranty: Manufacturer's standard form in which manufacturer agrees to furnish replacement components for fan units that demonstrate defects in workmanship or materials under normal use within warranty period specified.

Warranty Period: 12 months from startup or 18 months from shipment by manufacturer, whichever first occurs.

PRODUCTS

MANUFACTURER

Basis-of-Design Manufacturer: Provide fan units manufactured by Twin City Fan & Blower, Minneapolis MN; (763) 551-7600; email: tcf_sales@tcf.com; website: www.tcf.com.

Source Limitations: Obtain fiberglass propeller type wall exhaust fans from a single manufacturer.

PERFORMANCE REQUIREMENTS

Fan Performance Ratings: [Project site elevation- based] [Sea level elevation-based].

Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70.

FIBERGLASS PROPELLER WALL EXHAUST FANS

Description: Direct - driven, fiberglass, propeller type wall exhaust fans with wall mount panel.

Basis of Design Product: Twin City Fan & Blower, Model TCWPF.

Permanently attach nameplate displaying serial number and unit information.

Fan Capacities, Characteristics, and Configuration: Refer to Drawing schedule.

Propeller:

Provide propeller constructed with glass cloth impregnated with vinyl ester resin and secured to motor shaft.

Statically and dynamically balance propeller before and after assembling fan.

Wall Panel: Fabricate wall panel of resin and fiberglass, laminated with integral prepunched mounting flange on fan inlet side.

Provide solid FRP motor base, reinforced with solid FRP support struts.

Construct fan with ultraviolet (UV) and fire retardant resin. Maximum Flame Spread: 25, when tested in accordance with ASTM E84.

Motors: Fan motors shall be foot-mounted NEMA Design B, heavy duty industrial, continuous duty, variable-torque and shall be provided with the enclosure type, voltage, phase and hertz as listed in the fan schedule. Unless otherwise specified, all motors shall be equipped with ball bearings for heavy duty performance. Motor bearings shall have a minimum L-10 life, defined by AFBMA, of at least 40,000 hours (200,000 hours average life).

Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

Motor Speed: [1,800] [1,200] [900] rpm.

Specifier: Select motor electrical data in following subparagraphs, or show this data on the drawing fan schedule. Do not show the data in both places.

Specifier: Do not mix voltages between 60 Hz and 50 Hz values in following subparagraphs.

Electrical Data:

Voltage: [115] [208] [230] [277] [460] [575] [_____] V; [1] [3] phase; 60 Hz.

Voltage: [190] [380] V; [1] [3] phase; 50 Hz.

Full Load Amps: [_____] A.

Specifier: Select motor enclosure type in first following subparagraph.

Enclosure Type: [Open, Drip Proof (ODP)] [Totally Enclosed Fan Cooled (TEFC)] [Explosion Proof (EXP)].

Provide premium efficiency motor, suitable for inverter duty.

Specifier: For motors controlled by VFDs, retain following paragraph.

When required, provide premium efficiency motor, suitable for inverter duty, for motors controlled by Variable Frequency Drive (VFD).

Finishes:

Do not apply coatings to aluminum components/

After fabrication, clean and chemically pretreat ferrous metal parts by phosphatization.

Apply two coats of following finish:

Specifier: The first paragraph below is manufacturer's standard finish.  Those that follow are optional finishes.  Select finish that is required.

If fans specified for the project have different finishes, include the finish for each fan on the Drawings and delete here.

Air dry enamel.

Carbocoat 30

Hot Dip Galvanizing.

Plasite 4310 Vinyl Ester

Plasite 7122L Air Dry Phenolic

Heresite VR506 Air Dry Phenolic.

Dupont ASA, 70 Gray Polyester.

Accessories:

Specifier: Accessories listed in subparagraphs below are optional TCF features for this unit. Consult TCF representative for recommended options based upon Project requirements.

Safety Screens: Provide safety screens fabricated of [304] [316] stainless steel wire.

Provide screens at fan [inlet] [outlet].

Mounting Flange: Provide stainless steel mounting flange.

Provide stainless steel fasteners.

Static Grounding: Provide static grounding conductors and wire to single ground point, for field connection to building grounding system.

SOURCE QUALITY CONTROL

Factory Run Test: Test run assembled fan units prior to shipment at specified operating speed or maximum RPM allowed. Statically and dynamically balance each propeller in accordance with AMCA Standard 204 "Balance Quality and Vibration Levels for Fans" to Fan Application Category BV-3, Balance Quality Grade G6.3. Obtain balance readings by electronic equipment in the axial, vertical, and horizontal directions on each set of bearings.

Submit report of factory run test.

EXECUTION

EXAMINATION

Examine areas to receive fans. Notify Engineer regarding conditions that may adversely affect installation, operation, or maintenance of fans. Proceed with installation once conditions are in accordance with manufacturer's published instructions.

PROTECTION

Protect adjacent construction and finished surfaces during installation and testing.

Except for operational testing, do not operate fan during construction.

INSTALLATION

Install fans in accordance with Contract documents and manufacturer's published instructions.

Specifier: Insert applicable installation requirements for vibration, seismic, and high wind design if applicable to installation.

Install fan units with adequate clearances for service and maintenance.

Specifier: Coordinate duct installation and specialty arrangements with schematics on Drawings and with requirements specified in duct systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

Duct Connections: Drawings indicate general arrangement of ducts and duct accessories. Where indicated on Drawings, make final duct connections with flexible connectors. Flexible connectors are specified in Division 23 section "Air Duct Accessories."

Install connecting ducts with adequate clearances for service and maintenance.

Electrical Connections: Connect wiring in accordance with NFPA 70 and Division 26 section "Low-Voltage Electrical Power Conductors and Cables."

Ground and bond equipment according to Division 26 section "Grounding and Bonding for Electrical Systems."

Equipment Identification: Label units according to Division 23 section "Identification for HVAC Piping and Equipment."

FIELD QUALITY CONTROL

Specifier: Select option in paragraph below to define the party responsible for final tests and inspections to be performed.

[Owner will retain] [Contractor shall retain] qualified testing agency to perform field tests and inspections.

Specifier: Retain first paragraph below to describe tests and inspections to be performed.

Tests and Inspections:

Verify that unit is secured to supports, and that [duct and] electrical connections are complete. Verify that proper thermal-overload protection is installed in motors, starters, and disconnect switches.

Verify that cleaning and adjusting are complete.

Verify proper motor rotation direction, and verify fan propeller free rotation and smooth bearing operation

Verify that manual and automatic volume control, and fire and smoke dampers in connected ductwork systems are in fully open position.

Disable automatic temperature-control actuators, energize motor, adjust fan to indicated rpm, and measure and record motor voltage and amperage.

Shut unit down and reconnect automatic temperature-control actuators.

Remove and replace malfunctioning units and retest as specified above.

Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

Submit test and inspection reports.

ADJUSTING AND CLEANING

Adjust, clean, and maintain installed fan units in accordance with manufacturer's published instructions.

END OF SECTION